## PRELIMINARIES
GENERAL CONDITIONS AND PRELIMINARIRES ITEMS
S/N | DESCRIPTION | QTY | UNIT | RATE | AMOUNT
GENERAL CONDITIONS AND PRELIMINARIRES PRELIMINAIRES ITEMS
A | Insurance of works and equipment
B | Temporary Storage
C | Temporary electric power and lighting
D | Protecting of works and work site
E | Progress report and photograph
F | Shelters for the workmen etc
G | Transport for work people
H | Maintenance of public and private roads
I | Equipment mobilization and demobilization
J | Temporary fencing and gates
K | First aid equipment and services
L | Site meeting and report
M | Telephones
N | Scaffolding
O | Watching and security personel
P | Signboards / Signage
Q | Clear away rubbish
R | Concrete cube tests
S | Fire, polution and nuisance precaution
T | Prevention from storm and surface water
U | Site Accommodation
V | Temporary fence / Hoarding
| CARRIED TO GENERAL SUMMARY |  |  |  | 0

## UMTH Borno Unprice
ITEM | DESCRIPTION | QTY | UNIT | RATE | AMOUNT
PROPOSED SUPPLY, REPAIRS, TESTING
AND COMMISSIONING OF OXYGEN PLANT AND
FITTINGS INSTALLATION WORKS AT UNIVERSITY
OF MAIDUGURI TEACHING HOSPITAL, BORNO STATE FOR
NATIONAL AGENCY FOR THE CONTROL OF AIDS (NACA)
INFORMATION
The contractor is hereby reminded of the
necessity to keep a qualified staff and duly
authorized by the principal on this work
as no variations would be entertained
COMPRESSOR
A | Supply and replace with KAESARSK25 + dryer or
| other equal and approved compressor | 1 | No
CHILLER MODEL [MOTIVAIR]
B | Overhaul and service existing Chiller | sum
C | Gas supply and refill | 40 | Kg
D | Supply, replace pressure control valve | 1 | No
OXYGEN GENERATOR [ASJ - 450]
E | Supply, replace and install Coalescing Filter | 1 | No
F | Supply and replace molecular sieve | 2 | drum
G | Supply, replace and install Particulate Filter | 1 | No
H | Supply, replace and install Feed Valves | 2 | No
I | Supply, replace and install Waste Valves | 2 | No
J | Supply, replace and install pressure guage | 2 | No
K | Supply, replace and install pressure regulator | 1 | No
L | Supply and replace Condensale drain valve | 4 | No
OXYGEN BOOSTER [RIX IND 2V3B]
M | Supply and replace one set of 6nos. O-rings | 1 | set
N | Supply and replace one set of 6nos.Compression Rings | 1 | set
O | Supply and replace one set of 6nos. Rider Ring | 1 | set
P | Supply, replace and install Piston Assembly | 1 | No
Q | Supply, drain and replace RIX Oil | 10 | liters
R | Supply, replace Line delivery tube heat exchanger | 1 | No
S | Supply, replace Line assembly check valve | 1 | No
MANIFOLD
T | Supply, replace / install Oxygen pigtail | 5 | No
U | Supply, replace / install Valve header | 5 | No
V | Supply, replace / install Filling Nuts | 5 | No
W | Supply, replace / install Pin Index adaptor | 3 | No
To Collection
ITEM | DESCRIPTION | QTY | UNIT | RATE | AMOUNT
A | Allow for additional spare parts to be procured
and stored up for periodic maintenance of
oxygen plant to be expanded as directed by
| the Supervising Consultants. Provisional Sum #4,800,000.00 | 1 | Sum
B | Allow for testing the installation to the
| satisfaction of Consultants. | 1 | No
C | Allow for commissioning the installation to the
| satisfaction of Supervising Consultants | 1 | No
D | Allow for removal of all unused accessories
| and clean and clear the hospital | 1 | No
E | Prepare and training of dedicated staff for routine operation of the facility gas plant. | 3 | Mnths
F | To Collection
COLLECTION
PAGE 1
PAGE 2
Carried to General Summary
PROPOSED SUPPLY, REPAIRS, TESTING
AND COMMISSIONING OF OXYGEN PLANT AND
FITTINGS INSTALLATION WORKS AT UNIVERSITY
OF MAIDUGURI TEACHING HOSPITAL, BORNO STATE FOR
NATIONAL AGENCY FOR THE CONTROL OF AIDS (NACA)
GENERAL SUMMARY
General conditions and Preliminaries
Proposed Repair of Oxygen Plants
SUB-TOTAL
TOTAL TO FORM OF TENDER
NAME OF CONTRACTOR: ------------------------------------------------------------------------------------------
ADDRESS:-----------------------------------------------------------------------------------------------------------------
COMPLETION PERIOD:----------------------------------------------------------------------------------------------
SIGNATURE:--------------------------------------------------------------------------------------------------------------
DATE:-----------------------------------------------------------------------------------------------------------------------