## COVER PAGE
NATIONAL AGENCY FOR THE CONTROL OF AIDS (NACA) WITH FUNDING FROM GLOBAL FUND
RENOVATION AND UPGRADE OF SELECTED CENTRAL MEDICAL STORES IN THIRTEEN LOCATIONS IN NIGERIA UNDER THE GLOBAL FUND RESILIENT & SUSTAINABLE SYSTEMS FOR HEALTH [RSSH] II PROJECT GRANT
LOT 2
PROPOSED RENOVATION AND UPGRADE OF CENTRAL MEDICAL STORE/WAREHOUSE AT DAMATURU, YOBE STATE
BILL OF QUANTITIES
MAY, 2022

## YOBE
ITEMS | DESCRIPTIONS | QTY | UNIT | RATE | AMOUNT
BILL Nr 1- PRELIMINARIESFOR PROPOSED RENOVATION AND UPGRADING OF DAMATURU, YOBE STATE MEDICAL STORES
BILL Nr 1 - PRELIMINARIES & GENERAL CONDITIONS
Project Sign- Board
A | Allow provisional sum for the provision, erection, maintenance and dismantling of project sign-board | 1 | sum
B | Scaffolding Allow for the Contractor's scaffolding requirements for the successful execution of the works | 1 | sum
Site Administration and Security
C | Allowances here shall cover for the costs of Site Adinistrative Staff (Supervisor, Clerk, Store-Keeper, etc) and all Contractors' site security personnel required for the duration of the project | 1 | sum
Water for the Works
D | Allowances here shall cover for the costs of all temporary water needs necessary for the execution of the Works | 1 | sum
E | Lighting and Power for the Works Allowance here shall cover for the costs of all temporary electricity/ power requirements for the successful execution of the works | 1 | sum
F | Insurance Declaration: On signing the contract, the contractor shall obtain from his insurers and lodge with PM a declaration that insurance provided is strictly in accordance with the contract |  | Sum
G | Safety, Health & Welfare Allow for the costs of providing all necessary safety gears for site workers and visitors alike (helments, boots, swimming jackets, eye goggles, gloves, ear protection gears etc); provision of medicaments (iodine, crape and ordinary bandages, hydrogen peroxide, analgesics, etc) in a first aid box; and such other facilities that are necessary for the welfare of the workforce, in the course of carrying out the Works | 1 | sum
H | Progress Photographs Allow for the providing 5 sets of 12 No. 10'' × 5" progress photographs to be submitted monthly during the course of the project (Hard and Electronic) | 1 | sum
BILL NR.1: PRELIMINARIES
| TOTAL CARRIED TO GENERAL SUMMARY |  |  | ₦
BILL NR. 2: PROPOSED RENOVATION AND UPGRADING OF PLATEAU STATE CENTRAL MEDICAL STORE (STORE A)
ALTERATION AND IMPROVEMENT
(ALL QUANTITIES ARE PROVISONAL)
Information
The work in this section comprises of alterations and improvement to existing property with strict compliance to the NPSCMP directive
Alterations and improvement works
A | Carefully remove existing roofing covering with all structural steel members and cart away debris from site | 98 | m2
B | Carefully remove without making any defect on the building and cart away from site the following Windows; 1200×1000mm high | 14 | Nr
C | Carefully pull down existing partitions in office and external walls area and make good surfaces disturbed | 154 | m2
D | Pull down existing reinforced slab and cart away debrish from site | 533 | m2
E | Carefully scrap and remove the faded wall paint without making any defect on the affected area in the building | 628 | m2
F | Carefully scrap the existing dilapidated floor screeding (Main Store) and remove the debris away from site without making any defect on the affected area in the building | 567 | m2
G | Allow a provisional sum of ₦100,000.00 for cleaning and carting away of all rubbish and dirt in the building ready for works | 1 | sum
ALTERATION AND IMPROVEMENT
| Carried to Summary |  |  | ₦
NEW WORK
1.5: Excavation and filling
Site Preparation
A | Excavate foundation trench to receive walls and drains not exceeding 2.00 metres deep, commencing at strip level, including all working spaces | 183 | m3
B | Excavate pit to receive column bases not exceeding 2.50 metres deep, commencing at strip level, including all working spaces | 124 | m3
C | Laterite filling to make up under floor well rammed and compacted in 150mm layer | 1280 | m3
D | Backfiling around foundation and bases, deposited and well compacted in 150mm layers | 123 | m3
E | Disposal; excavated materials off site; exceeding 100mm and deposit, spread and level where directed | 184 | m3
Approved imported hardcore laterite filling
F | Level and compact bottom of excavation and bases to receive concrete | 270 | m2
G | 300mm imported hardcore (crushed rock laterite) filling in making up levels under building, deposited, watered and well compacted with eight passes of 8T roller | 371 | m3
H | Prepare and apply Dieldrex anti-termite solution or similar equal and approved treatment to surfaces of excavation | 660 | m2
Damp-proof membrane
J | One layer of 250micron damp proof membrane laid on hardcore and lapped at sides and ends | 1235 | m2
1.11: In situ concrete
In- situ concrete - 5N/mm2
K | 50mm blinding bed under column bases | 6 | m3
L | 50mm blinding bed under bed | 61 | m3
TO COLLECTION
CONCRETE WORK
STRUCTURAL REINFORCED CONCRETE
In-situ reinforced concrete - 15N/mm2
A | Coumn base | 49 | m3
B | Stub columns | 11 | m3
C | Ground beam | 17 | m3
D | Foundation base | 35 | m3
E | 150mm horizontal bed / steps | 185 | m3
1.11. 34: Reinforcement for in situ concrete
Round mild steel bar reinforcement to B.S. 4449, including all hooks, bends, distance blocks, trying wire etc.
F | 10mm - 20mm diameter bars | 13090 | kg
G | Wire mesh | 1235 | m2
1.11.13: Formwork for insitu concrete
Formwork class 'F1'''(Wrought hardwood)
H | Vertical sides column | 104 | m2
J | Sides of ground beam | 74 | m2
K | Vertical sides of bases thickness 350-500mm / Ramp | 84 | m2
L | Vertical edge of ground slab 150mm wide / Ramp | 124 | m
1.14: Brick/Block walling
Sandcrete hollow blocks with cavities filled solid with concrete prescribed mix Grade 15 in plasticised cement mortar (1:3)
M | 225mm wall | 415 | m2
N | Allow a sum for additional sub structure works as may be expended as directed
TO COLLECTION
COLLECTION
Page 3
Page 4
SUB STRUCTURE CARRIED TO SUMMARY
ELEMENT NO.2 - CONSTRUCTION OF REINFORCED CONCRETE FRAME STRUCTURE
1.11: In situ concrete
STRUCTURAL REINFORCED CONCRETE
In- situ reinforced concrete Mix "A'' - 15N/mm2
A | Column | 8 | m3
1.11.34: Reinforcement for in situ concrete
Round mild steel bar reinforcement to B.S. 4449, including all hooks, bends, ditance blocks, tying wire etc.
B | 10- 16 diameter bar | 1572 | kg
1.11.13 : Formwork for in situ concrete
Formwork Class "F2" ( Sawn Hardcore)
C | Vertical sides of column | 137 | m2
1.15 : Structural steel framing
Fabricate stell work grade 43C; BS 4360 framed work Comprising stantion beams, fixing accessories etc to structural Engineers drawings
D | 250 ×250 X 10mm UB stanchion | 195 | m
E | 180 ×180 × 8mm UB Beam | 124 | m
Sundries
F | 300 ×350 × 25mm thick mild steel base plate with 4NO.27mm diameter holes and 25mm diameter black bolts 600mm long with nuts and washers | 20 | No
G | 145 ×200 × 12mm thick stiffener plates | 20 | No
H | 133 ×203 × 20mm thick mild steel plate welded to UB (measured seperately) with 6mm continuous fillet 6No. 16mm diameter hole for 6No. M14 Grade 8.8 bolts | 20 | No
J | Holding down assembly comprising of 25mm diameter black bolts 500mm bent at end and fixed 76mm diameter tubes 325mm long; all gronted in concrete | 80 | No
Painting
Prepare, rub down all rust mill scale and apply one undercoat of red oxide primer
K | Structured steelwork before erection | 319 | m
CONSTRUCTION OF REINFORCED CONCRETE FRAME CARRIED TO SUMMARY
ELEMENT NO.03: UPPER FLOOR
1.11: In situ concrete
In - situ reinforced concrete Mix G15
A | 150mm thick slab | 11 | m3
B | Beam | 18 | m3
1.11.34: Reinforcement for in situ concrete
Round mild steel bar reinforcement to B.S. 4449, including all hooks, bends, distance blocks, tying wire
C | 10 -16 diameter | 5220 | kg
1.11.13: Formwork for in situ concrete
Plain fair face formwork to;
D | Soffit of slabs | 89 | m2
E | Sides and soffit of beam | 186 | m2
F | Vertical edge of slab 150mm wide | 44 | m
UPPER FLOOR CARRIED TO SUMMARY
ELEMENT NO. 4: SANDCRETE HOLLOW BLOCK WORK
GENERALLY
Scope
1.14: Brick/Block walling
Sandcrete hollow blocks in plasticised cement mortar (1:3)
A | 150mm wall | 65 | m2
B | 230mm wall | 1850 | m2
1.11: In situ concrete
Reinforced in situ concrete (1:2:4) in: Isolated beams
C | lintels/beams on walls; continuous beam | 7 | m3
1.11.13: Formwork for in situ concrete
Plain fair face formwork to;
D | lintels; sides/soffits | 89 | m2
1.11.34: Reinforcement for in situ concrete
High tensile deformed round bar reinforcement to BS 4449
E | 10 - 16mm diameter bar | 1050 | kg
SANDCRETE FOLLOW BLOCKWARE CARRIED TO SUMMARY
ELEMENT NO.5 - STRUCTURAL STEEL FRAMEWORK FOR ROOF STRUCTURE AND COVERING
1.11: In situ concrete
Reinforced in situ concrete (1:2:4) in: Isolated beams
A | Roof beams on walls; continuous beam | 7 | m3
1.11.13: Formwork for in situ concrete
Plain fair face formwork to;
B | Roof beam sides | 57 | m2
1.11.34: Reinforcement for in situ concrete
High tensile deformed round bar reinforcement to BS 4449
C | 10 - 16mm diameter bar | 1050 | kg
1.15: Structural steel framing
Structural steelwork fabricated steelwork grade 43; BS 4360, work shop fabricated, site welded the following in 20No. Roof trusses spaning 20.12m with a rise of 2.50m
D | 150 ×150 × 8mm UB as Rafter | 692 | m
E | 75 × 75 × 6mm Angle welded to rafters | 675 | m
F | 200 × 150 × 8mm stiffener plate | 48 | No
G | 12mm diameter High yield deformed bar as Anti-sag rod | 48 | m
H | 16mm gusset plate | 38 | No
J | C' Purlins size 100 x 75 x 4mm | 1110 | m
K | 135 × 75 × 8mm thick angle cleat 200mm Long | 559 | No
L | Allow for other accessories for the roof trusses |  | Item
Painting
Prepare, rub down all rust mill scale and apply one undercoat of red oxide primer
J | Structural steelwork before erection | 1367 | m
TO COLLECTION
1.17 SHEET ROOF COVERING
0.55mm coloured longspan deep Trough Profile Aluminium sheeting double lapped and fixed in accordance with the manufacturers instructions (measured nett)
A | Insulated Roofing sheet | 1269 | m2
B | Ditto: but without insulation; Fasia / External ceiling | 235 | m2
C | Ridge cap 600mm girth | 33 | m
To Collection
COLLECTIONS
Page 8
Page 9
STRUCTURAL STEEL FRAMEWORK FOR ROOF STRUCTURE AND ROOF COVERING CARRIED TO SUMMARY
ELEMENT NO. 6: STAIRCASE
1.11: In situ concrete
In-situ concrete -5N/mm2
A | 50mm blinding under staircase ground beam | 1 | m3
In-situ reinforced concrete Mix "A'' - 15N/mm2
B | Staircases | 6 | m3
1.11.34: Reinforcement for in situ concrete
High tensile deformed round bar reinforcement to BS 4449
C | 10 - 16mm diameter bar | 600 | kg
1.11.13: Formwork for in situ concrete
Formwork class "F1" (Wrought hardcore)
D | Sloping soffit of staircase | 14 | m2
E | Soffit of landing | 5 | m2
F | Edge of landing not exceeding 300mm wide | 15 | m
G | Riser of steps not exceeding 300mm wide | 38 | m
H | Outer string of staircase not exceeding 300mm wide | 21 | m
Steel; High impact nylon sleeve over continous 'corrosion resistant steel core balustrades to Architects' instructions
J | Balustrades and handrails
| 1200 high; comprising 40 diameter balusters at 1.20m centres plugged and screwed to concrete floors or teps, 40 diameter handrail and 10 thoughened glass infill panels with rounded corners and polished edges | 15 | m
STAIRCASE CARRIED TO SUMMARY
ELEMENT NO. 7: DOORS AND WINDOWS
1.23:WINDOWS, SCREENS AND LIGHTS
Supply and fix the following color coated glazed aluminium windows or similar approved complete with all 6mm thick glazing, ironmongery and fixing to concrete or blockware and pointing all round with approved mastic sealing compound in accordance with the manufacturers details
A | Sliding window overall size 1500 ×1200mm high | 1 | No
B | Ditto; overall size 1200 × 1200mm high | 2 | No
C | Ditto; overall size 2400 × 600mm high | 2 | No
D | Ditto; overall size 1200 × 600mm high | 12 | No
E | Projected window overall size 600 × 600mm high | 4 | No
1.24 DOORS , SHUTTERS AND HATCHES
F | Purpose made security steel door overall size 1500 × 2100mm high including all accessories | 1 | No
G | Ditto; size 1200 ×2100mm high including all accessories | 1 | No
H | Ditto; size 900 ×2100mm high including all accessories | 6 | No
J | Purpose made flush door overall size 750 × 2100mm high complete with frames and all ironmongeries | 4 | No
K | Purpose made immergency push-back steel door overall size 1500 × 2100mm complete | 2 | No
L | Purpose made steel gate overall size 2400 × 2500 complete | 2 | No
DOORS AND WINDOWS CARRIED TO SUMMARY
ELEMENT NO.8 FINISHES
1.28 FLOORS, WALLS, CEILINGS AND ROOF FINISHINGS
FLOOR FINISHES
1.28.2: SAND CEMENT/CONCRETE/SCREEDS/TOPPINGS
A | 50mm thick; screded to receive epoxy finish | 820 | m2
B | 42mm thick; to receive floor tiles | 152 | m2
C | Supply and apply 2 coats of epoxy paints on power floated floor | 820 | m2
TERRAZZO FLOOR FINISHES
Insitu Terrazzo floor finishes in approved colour aggregate/chippings size laid on 25mm cement and sand base in bay 1500x1500mm divided with ebonite strip both side with and including polishing on complete
D | Floor; 25mm thick level and falls only to screeded in loading bay and entrance staircase | 75 | m2
E | Ditto skirting; internally; 100mm high | 21 | m
Stone/Concrete/Quarry/CeramicTiling/Mosaic
Ceramic Tiling; Ceramic floor tiling in approve colour
patterned;fixing with approved adhesive; pointing
with matching grout including screeded backing ;
floors 400x400x8mm nominal size;
F | Tiling; internally; over 300mm wide in selected | 152 | m2
compartments.
G | Ditto skirting; internally; 100mm high | 95 | m
WALL FINISHES
1.28.7: PLASTERED/RENDERED/ROUGHCAST COATINGS
Mortar, cement and sand (1:4): steel trowelled 12mm work to walls on concrete base or blockwork
H | Width exceeding 300mm wide | 1100 | m2
J | Ditto: not exceeding 300mm wide | 94 | m
TO COLLECTION
EXTERNALLY
1.28.7: PLASTERED/RENDERED/ROUGHCAST COATINGS
Mortar, cement and sand (1:4): steel trowelled 12mm work to walls on concrete base or blockwork
A | Width exceeding 300mm wide | 1197 | m2
B | Ditto: not exceeding 300mm wide | 67 | m
INTERNALLY
Cement and sand mortar (1:4): steel trowelled,
C | 15mm thick work to walls on concrete base or blockwork width exceeding 300mm | 2180 | m2
D | Width exceeding 300mm | 124 | m
E | Floating with POP Screed; Width exceeding 300mm wide | 2180 | m2
F | Ditto: not exceeding 300mm wide | 124 | m
Screeded backing; 12mm thick; over 300mm wide
Walls
G | to receive ceramic tiles | 240 | m2
H | surface n.e 300mm wide | 82 | m
Stone/Concrete/Quarry/Ceramic Tiling/Mosaic
Ceramic Tiling;glazed cushioned edge 'spanish'
wall tiling 250x450x6mmthick nominal size; fixing
with cement and sand mortar; pointing with cement
on screeded backing (measured separately)
J | Walls | 240 | m2
K | surface n.e 300mm wide | 82 | m
CEILING FINISHES
L | Supply and install 8mm thick gypsum board an a metal or steel grid (included) at a spacing of 600 × 600mm centres on both side | 1230 | m2
TO COLLECTION
COLLECTION
Page 12
Page 13
FINISHINGS CARRIED TO SUMMARY
ELEMENT NO.9 PAINTING AND DECORATIONS
SURFACE FINISHES
INTERNALLY
1.29: PAINTING/ CLEAR FINISHING
Suppy and apply 2 coats of high quality satin painting to general surfaces of existing walls ˃300mm girth internally including all preparation of surfaces and screeding work on;
Cement rendered general surfaces
A | Girth exceeding 300; wall | 2036 | m2
B | Ditto: not exceeding 300mm wide | 187 | m
EXTERNALLY
Cement rendered general surfaces
C | Ditto: But Texacote paint Girth exceeding 300; wall | 836 | m2
D | Ditto; not exceeding 300mm wide | 90 | m
PAINTING AND DECORATIONS CARRIED TO SUMMARY
ELEMENT NO.10 FITTINGS AND FIXTURES
Racks
Supply, install and commission the following heavy duty industrial pharmaceutical warehouse equipments produce by spangle steel or other approved brands
A | Provide and install heavy duty warehouses racks and shelves over size 5000 × 900 × 3500mm high at the MCDURCH CONSTRACTING LIMITED on +234-808-073-5141 | 20 | Nr
B | Mobile-Step-Ladder | 2 | Nr
C | Hydraulic hand pallet truck/trolley; capacity; 3-tonnes | 2 | Nr
D | Plastic Pallets | 10 | Nr
WAREHOUSE OPERATION SOFTWARE/OFFICE EQUIPMENTS
E | Allow for the supply, installation Warehouse/store operation management software. Two (2) Units Desktop Computer, One (1) unit of Laptop. One (1) unit of HP printer and one (10 unit of Hp photocopier | 1 | Nr
F | Supply, off load an assemble manual forklift stacker with a lift height not exceeding 2M and 2000kg lift capacity | 3 | Nr
G | Ditto: But hydraulic hand truck Trolley cart weight 3000kg | 3 | Nr
H | Provide and install mobile steel ladder of height 5m high | 2 | Nr
REFRIGERATIONS
J | Supply and install thermocool SKD SC240 R6 show case refrigerator or equal and approve quality 240L capacity | 6 | Nr
FREEZERS
K | Suppy and instal Haier Thermocool 729L Large chest freezers HTF-719R6 WHT or equal and approve as directed | 6 | Nr
L | Supply and install fire hydrant and horse reel | 2 | Nr
PIPE WORK
M | Allow for general pipe work as may deemed necessary | 1 | Nr
To Collection
TEMPERATURE AND HUMIDITY EQUIPMENT
A | Supply and install digital combine temperation and humidity guage for the warehouse use | 6 | Nr
COMPUTER
B | Supply and install software for the warehouse, HP all-in-one desktop computer., 200 G3 core i5 1TB 4g 215'' DVD WIFI W10 PRO for administrative use, HP 15 - dao407, intel pentinum Silver 4G RAM, 1TB HDD, Windows 10, HP Deskjet, 3835 all-in-one printer F5R96C | 1 | nr
C | Supply, assemble and install 150kva penkins or equal amd approved electric generating set, including cables not more than 30mtrs to connect it to switch over, all necessary excavation and chase, concrete plinth and shade | 1 | nr
SOLAR LIGHTING
D | Supply, assemble and install 200w all-in-one LED street solar light this includes excavation, concrete base and all necessary | 10 | nr
CCTV
E | Supply and install CCTV systems, 24 channels comprises of 42'' HD monitor, dome weather proof 6 colour cameras with night vision 50 meter radius and DVR AHD with 6HDD in warehouses | 1 | nr
To Collection
Collections
Page 15
Page 16
FITTINGS AND FIXTURES
Total Carried to summary
ELEMENT NO.11 MECHANICAL INSTALLATIONS
Information
Nature and location of the work; the work in this section comprises: (i) drainageand cold water pipe work, fire fighting installation and Airconditioning installation
N13 SANITARY FITTINGS
N13 SANITARY APPLIANCES/FITTINGS
ARMITAGE SHANK OR OTHER APPROVED SANITARY APPLIANCES/ FITTINGS EQUIPMENT, APPLIANCES AND FITTINGS ASSOCIATED WITH SERVICES: SUPPLY, ASSEMBLE AND FIX AS INDICATED IN ENGINEER's DRAWINGS. RATE TO INCLUDE FORJOINTING TO WATER SUPPLY AND DISCHARGE PIPES
A | Close couple water closet, complete with fittings including nessary installation accessories | 8 | nr
B | Wash hand basin, complete with pedestal; plastic bottle trap, overflow chain, stay and black plastic plug, pair of 13mm chromium plated easy clean pillar taps to B.S 1010; complete fittings; as Engineer's specification | 8 | nr
C | Floor drain: 50mm stainless steel; 50mm drawn copper S-trap, mounted flush with floor finish; with galvanized wire strainer; as Engineer's specification | 8 | nr
D | Toilet roll holder; plastic roller and chronium plated body, length 100mm screwed to wall with and including drive screws; as Engineer's Specification | 8 | nr
E | Stainless steel soap dispenser fixed to wall | 8 | nr
F | Mirror; 4mm silvered float glass; 600×600mm; with arised edges; mounted on walls with and including chromium plated dome-headed drive screws | 8 | nr
G | Allow a provisional sum for all piping work to be expended as directed. |  | Sum |  | 800000
AIR-CONDITIONING/VENTILLATION INSTALLATIONS
U11 TOILET EXTRACTOR FANS EXTRACT UNITS XPELAIR, WOODS OR OTHER APPROVED EQUAL SUPPLY WITH 1.5MM2 3-CORE PVC SHEATED AND INSULATED COLOUR CODED COPPER CABLE AND 5A 3-PIN PLUG; MOUNTING TO STRUCTURE
H | Wall mounted fan; 50Hz; 240V; Extract Capacity 90m3/h; ditto for external building toilets. | 8 | nr
MEHANICAL INSTALLATIONS
To Collections
MECHANICAL INSTALLATIONS CONT'D
A/C AND VENTILATION SYSTEM INSTALLATIONS
Supply, install, test and commission free standing split air conditioning unit complete with its outdoor unit and all necessary integrated controls and infra-red remote control. PANASONIC, SAMSUNG, MIDEA, LG, DAIKIN or approved equal
A | Cooling capacity: 36,000 Btu/hr (18Kw) | 6 | nr
Supply, install, test and commission high wall mounted split air conditioning unit complete with its outdoor unit and all necessary integrated controls and infra-red remote control. PANASONIC, SAMSUNG, MIDEA, LG, DAIKIN / equal equivalent
B | Cooling capacity: 18,000 Btu/hr | 4 | nr
C | Cooling capacity: 12,000 Btu/hr | 8 | nr
S71 FOAM FIRE FIGHTING
Y21 FIRE EXTINGUISHERS
EQUIPMENT, SUPPLY, ASSEMBLE AND INSTALL; RATE TO INCLUDE FOR CONNECTIONS TO PIPELINES; SUPPLY WITH ALL MECHANICAL AND ELECTRICAL FITTINGS ACCESSORIES, ANCILLARIES AND CONTROL COMPONENTS DEEMED NECESSARY FOR A COMPLETE INSTALLATION
Fire extinguisher; hand held; lever operated; to B.S. 5423; ready charged; red painted; with mounting bracket plugged and screwed to wall;
D | Multi- purpose foam type; 9.0 litres capacity; compressed air; class ABC fires (fire rating 5A & 34B) | 11 | nr
E | ditto 5kg CO2 Fire extinguisher | 9 | nr
S71 FOAM FIRE FIGHTING
COLD ROOM
CHILLERS
G | Supply, off load and replace attached FOSTER chillers with 2.2kw compressor, R404A Refrigerant and tested pressure of 30bar. Serial No. 0917387G | 2 | Nr
To Collection
Collections
Page 17
Page 18
MECHANICAL INSTALLATIONS
Carried to General Summary
ELECTRICAL INSTALLATIONS
V: ELECTRICAL SUPPLY/ POWER/LIGHTING
Information
Nature and Location of the work
The work in this section comprises:
(i) the installation of all work within the internal and external faces of building, up to and including distribution boards, cables light fittings, air conditioners, extractor fans, fire alarms, closed circuit television and communication installations together with associated wiring, conducting and wall switches
(ii) The description of the measured items are not necessarily fully comprehensive but are intended to indicate the particular item of work concerned. The price for the works allows for, conduits, wiring, earthing connection etc. to ensure that the electrical installations functions in such a maaner as to satisfy all the statutory, regulations of Nigeria and the relevant local government institutions and professional bodies
V: ELECTRICAL SUPPLY/POWER/ LIGHTING SYSTEMS
A | Allow a provisional sum of ₦3,000,000.00 (Three Million naira only) for the insatllation, testing and commissioning of closed circuits television |  | Sum
W20 TV/CCTV
CLOSED CIRCUITS TELEVISION CAMERA/ SURVELLANCE
Equipment: supply, install, connect up and commission CCTV/SURVELLANCE equipmentas manufactured by SONY, BOSCH or other approved complete with all accessories to form a complete system
B | Allow a provisional sum of ₦1,000,000.00 (One Million Naira only) for the installation, testing and commisioning of closed circuits Television Cameras |  | item
ELECTRICAL INSTALLATIONS:
Total Carried to Summary
SUMMARY
A | DEMOLITION, ALTERATION, REPAIRS AND CONSERVATION
B | SUB STRUCTURE
C | CONSTRUCTION OF REINFORCED CONCRETE FRAME STRUCTURE
D | UPPER FLOOR
E | SANDCRETE HOLLOW BLOCK WORK
F | ROOF STRUCTURE AND COVERING
G | STAIRCASE
H | DOORS AND WINDOWS
J | FINISHES
K | PAINTING AND DECORATIONS
L | FURNITURE, FITTINGS AND EQUIPMENT
M | MECHANICAL INSTALLATIONS
N | ELECTRICAL SERVICES INSTALLATIONS
TOTAL FOR MEDICAL STORE/OFFICE TO GENERAL SUMMARY
1.35 SITE WORKS
1.5: Excavation and filling.
A | Shape; and compact sub- grade formation to 100% B5 compaction prior to laying of sub-base | 1200 | M2
1.11: In situ Concrete
Mixing/casting/curing/in-situ concrete
Reinforced in situ concrete (1:3:6) 19mm aggregates filled into formwork, vibrated and curd: generally in:
B | Pavings slab not exceeding 100mm thick: laid to fall and cross falls in alternate bays of 2500mm ×2500mm (maximum): rates to include form work between bays, brushed surfaced finish | 1200 | M2
1.11.37: Reinforcement for in situ concrete
C | Fabric mesh reinforcement, type A143 weighing 1.45kg/m2 (4mm) laid in concrete floor beds with 150mm side and end labs (measured net no allowance made for labs) | 1200 | M2
SITE WORKS CARRIED TO SUMMARY

## SUMMARY
ITEMS | DESCRIPTIONS | QTY | UNIT | RATE | AMOUNT
GENERAL SUMMARY
Naira
1 | PRELIMINARIES
2 | STORE/WAREHOUSE
3 | SITE WORKS/EXTERNAL WORKS
SUB-TOTAL
a | CONTINGENCY |  |  |  | 10000000
SUB-TOTAL
b | ADD VAT 7.5%
| AMOUNT TO TENDER |  |  | ₦